## Assessment Summary
Unit of Assurance — Assessment Summary
Project Name | COU Name | COU Description | Profile | Device Class | Model Risk Level | Assurance Level | Standards Reference | Assessor Name | Assessment Date | Source Document | Has UQ?
AHU Ducted Axial Fan CFD – Pressure Rise and Flow Uniformity | Predict total pressure rise and outlet flow uniformity for 500 mm axial fan at 1200 RPM in AHU plenum to support equipment selection | Steady RANS CFD (Ansys Fluent 23.2, MRF) of a ducted axial fan in an air-handling unit plenum. The model predicts total pressure rise across the fan/diffuser and outlet swirl intensity and flow non-uniformity at the grille plane at three duty points (2.0, 3.0, 4.0 m^3/s). Results are used to confirm whether the 500 mm fan at 1200 RPM meets the ≥250 Pa / ≤0.20 swirl / ≤0.35 non-uniformity requirements before equipment selection. Scope excludes acoustics, structural response, icing, and motor thermal modeling. | Complete | N/A | MRL 3 | Medium | ASME-VV40-2018 |  | Date of this assessment (YYYY-MM-DD) | DOI, report number, or URI | Yes
Legend: |  | Required (Minimal) | Required (Complete) | Optional
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on C3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%
Note on F3: [Extract] ¦ Confidence: 50%
Note on G3: [Extract] ¦ Confidence: 50%
Note on H3: [Extract] ¦ Confidence: 50%
Note on L3: [Extract] ¦ Confidence: 50%

## Instructions
UofA Excel Template — Instructions
What is this? | This workbook captures a credibility assessment for one Context of Use (COU). Fill it out, then run `uofa import` to convert it to a machine-verifiable evidence package.
One workbook = one COU | If your project has multiple COUs (e.g., different device classes or risk levels for the same model), create a separate workbook for each.
Profiles | Minimal (7 fields, lightweight audit trail) is for early-stage projects or live pipeline capture. Complete (full V&V 40 assessment) is for regulatory submissions.
Color coding | Blue cells = required for Minimal profile. Green cells = required for Complete profile. White cells = optional.
Credibility Factors | Sheet 4 is pre-populated with all 13 V&V 40 factors from Table 5-1. You do not need to assess all 13 — set Assessed = "No" or "N/A" for factors not relevant to your COU.
Dropdowns | Most constrained fields use dropdown lists. If you need a custom value not in the dropdown, type it directly (the validation will warn but not prevent entry).
After filling out | Run: uofa import your-file.xlsx --sign --key keys/your.key --check
What the tool checks | Gate 1 (SHACL): Are all required fields present? Gate 2 (Jena rules): Are there quality gaps (weakeners)? Gate 3 (Integrity): Is the hash and signature valid?
More info | https://crediblesimulation.com ¦ https://github.com/cloudronin/uofa

## _Lists (hidden)
Profile | Device Class | Model Risk Level | Assurance Level | Standards Reference | Entity Type | Has UQ | Pass/Fail | Factor Level (1-5) | Factor Status | Decision Outcome | Has UQ (COU-level)
Minimal | Class I | MRL 1 | Low | ASME-VV40-2018 | Requirement | Yes | Pass | 1 | assessed | Accepted | Yes
Complete | Class II | MRL 2 | Medium | NASA-STD-7009B | Model | No | Fail | 2 | not-assessed | Not accepted | No
| Class III | MRL 3 | High | FDA-2023-CMS | Dataset |  | Inconclusive | 3 | scoped-out | Conditional
| Category A | MRL 4 |  | Custom |  |  | N/A | 4 | not-applicable
| Category B | MRL 5 | [5 empty] | 5
Category C
Category D
Category E
Other

## Model & Data
Model & Data — What you modeled and compared against
Entity Type | Name | Identifier / URI | Description | Version | Source
Requirement | Fan Performance Acceptance Criteria | Stable URI or local ID | Δp_total within ±5% at 3.0 m^3/s and ±8% at 2.0 and 4.0 m^3/s; swirl intensity ≤0.20 at grille plane; non-uniformity index ≤0.35 at grille plane | Version number (optional) | Where this came from (optional)
Model | Ansys Fluent 23.2 Steady RANS MRF Model |  | Double-precision Fluent 23.2 with poly-hexcore meshing (ICEM + Fluent mesher), k-ω SST turbulence closure, MRF rotating zone, incompressible pressure-based coupled solver; transient sliding-mesh spot-check at design point
Dataset | AMCA 210 Vendor Test Data (Report F-210-663) |  | AMCA 210 test stand fan performance data at three duty points corrected to 25°C and sea level; includes calibration sheets for pressure taps and flow nozzle; Δp uncertainty ±1.5%, flow ±1.0%, RPM ±0.3%
Dataset | Vendor Fan CAD and AHU Plenum Geometry |  | Impeller and shroud CAD from vendor dated 2026-05-11; AHU plenum geometry from project Rev C; tip clearance 1.5 mm per vendor drawing
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on A4: [Extract] ¦ Confidence: 50%
Note on B4: [Extract] ¦ Confidence: 50%
Note on D4: [Extract] ¦ Confidence: 50%
Note on A5: [Extract] ¦ Confidence: 50%
Note on B5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on A6: [Extract] ¦ Confidence: 50%
Note on B6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%

## Validation Results
Validation Results — What you found when you tested the model
Result Name | Identifier / URI | Description | Compares To | Has UQ? | UQ Method | Metric Value | Pass / Fail
Mesh Convergence / Resolution Study | ValidationResult | What was done, what was found | Three-mesh poly-hexcore resolution study (coarse 1.5 M, medium 4.2 M, fine 12.7 M cells) at design point 3.0 m^3/s; Richardson extrapolation apparent order p≈1.9; GCI-style uncertainty (Fs=1.25) computed between medium and fine meshes | Richardson extrapolation / GCI reference value | Yes | Richardson extrapolation with GCI (Fs=1.25) | GCI 1.9% on Δp_total (medium vs fine); medium within 2% of fine for Δp, within 0.01 absolute for swirl | Pass
CFD vs AMCA 210 Test Data – Operating Map Comparison | ValidationResult |  | Comparison of CFD-predicted total pressure rise to AMCA 210 test stand measurements at three duty points (2.0, 3.0, 4.0 m^3/s); fine mesh used at design point, medium elsewhere | AMCA 210 vendor test data (Report F-210-663, 2026-06-07) | Yes | Experimental uncertainty propagation (Δp ±1.5%, flow ±1.0%, RPM ±0.3%) | 2.0 m^3/s: −6.5%; 3.0 m^3/s: −3.2%; 4.0 m^3/s: −3.1% | Pass
Turbulence Model Sensitivity Study | ValidationResult |  | Comparison of k-ω SST, Spalart–Allmaras, and Realizable k-ε at design point on medium mesh; evaluated for Δp_total and swirl intensity; SST selected for best tip leakage vortex agreement with lab PIV visuals | Lab PIV qualitative traverses and inter-model comparison | No |  | SST vs RKE Δp spread 1.5%; SA under-predicts by ~1.8% | Pass
Steady MRF vs Transient Sliding-Mesh Spot-Check | ValidationResult |  | Transient sliding-mesh run at design point (2° time step) compared to fine steady MRF result; time-averaged Δp and swirl intensity compared | Fine-mesh steady MRF prediction | No |  | Δp difference +1.1% (261.4 vs 258.5 Pa); swirl 0.20 vs 0.19 | Pass
Input Sensitivity Analysis | ValidationResult |  | Parametric sensitivity runs varying inlet turbulence intensity (1–10%), blade surface roughness (0 vs 50 μm), tip clearance (±0.3 mm), and RPM (±1%) around baseline design point conditions | Baseline medium-mesh design-point prediction | Yes | One-at-a-time parameter perturbation | TI: Δp −0.8% to +1.5%; roughness: Δp −0.6%; tip clearance: Δp −2.1% to +1.7%; RPM ±1%: Δp ±2.0% | Pass
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on D3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%
Note on F3: [Extract] ¦ Confidence: 50%
Note on G3: [Extract] ¦ Confidence: 50%
Note on H3: [Extract] ¦ Confidence: 50%
Note on I3: [Extract] ¦ Confidence: 50%
Note on A4: [Extract] ¦ Confidence: 50%
Note on B4: [Extract] ¦ Confidence: 50%
Note on D4: [Extract] ¦ Confidence: 50%
Note on E4: [Extract] ¦ Confidence: 50%
Note on F4: [Extract] ¦ Confidence: 50%
Note on G4: [Extract] ¦ Confidence: 50%
Note on H4: [Extract] ¦ Confidence: 50%
Note on I4: [Extract] ¦ Confidence: 50%
Note on A5: [Extract] ¦ Confidence: 50%
Note on B5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on E5: [Extract] ¦ Confidence: 50%
Note on F5: [Extract] ¦ Confidence: 50%
Note on H5: [Extract] ¦ Confidence: 50%
Note on I5: [Extract] ¦ Confidence: 50%
Note on A6: [Extract] ¦ Confidence: 50%
Note on B6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on E6: [Extract] ¦ Confidence: 50%
Note on F6: [Extract] ¦ Confidence: 50%
Note on H6: [Extract] ¦ Confidence: 50%
Note on I6: [Extract] ¦ Confidence: 50%
Note on A7: [Extract] ¦ Confidence: 50%
Note on B7: [Extract] ¦ Confidence: 50%
Note on D7: [Extract] ¦ Confidence: 50%
Note on E7: [Extract] ¦ Confidence: 50%
Note on F7: [Extract] ¦ Confidence: 50%
Note on G7: [Extract] ¦ Confidence: 50%
Note on H7: [Extract] ¦ Confidence: 50%
Note on I7: [Extract] ¦ Confidence: 50%

## Credibility Factors
Credibility Factors — V&V 40 Table 5-1 Assessment
Complete profile only. Assess each relevant factor: set Required Level (goal given model risk) and Achieved Level (what evidence supports).
Factor Type | Category | Required Level | Achieved Level | Acceptance Criteria | Rationale | Factor Status | Linked Evidence
V&V 40 factor (pre-filled, do not edit) | Grouping (pre-filled) | Credibility goal for this factor (1-5) | Level achieved by evidence (1-5) | Goal and basis for the required level (from V&V 40 Tables 3-4) | Brief justification (esp. if achieved < required) | assessed / not-assessed / scoped-out / not-applicable | URI of validation result that supports this factor (optional)
Software quality assurance | Verification — Code | 3 | 3 | Commercial solver with documented QA processes; version-controlled case and mesh management | Ansys Fluent 23.2 double-precision is a widely certified commercial solver with established QA processes. Mesh/case pairs are hash-checked and archived with run notes; Tecplot post-processing is scripted for repeatability. No explicit ISO certification documentation or internal regression test results are cited in the report, but use of a commercial solver at a specific pinned version with hash-checked meshes constitutes adequate QA evidence for MRL 3. | assessed
Numerical code verification | Verification — Code | 2 | 2 | Code correctly solves governing equations; benchmark or analytical comparison available | The report relies on Ansys Fluent as a commercially verified solver; no independent benchmark problems, MMS solutions, or analytical comparisons are reported within this study. The transient vs steady comparison provides an indirect cross-check. This constitutes basic code verification through commercial solver pedigree but no explicit code-level benchmark evidence is presented. | assessed
Discretization error | Verification — Calculation | 3 | 4 | Mesh convergence demonstrated; GCI or Richardson extrapolation reported; discretization uncertainty quantified | A three-mesh resolution study (1.5 M, 4.2 M, 12.7 M cells) was performed at the design point. Richardson extrapolation yielded apparent order p≈1.9. GCI-style uncertainty (Fs=1.25) between medium and fine meshes is 1.9% on Δp_total. Swirl intensity converges to within 0.01 absolute. Mesh quality metrics (non-orthogonality <70°, skewness P95 <0.26, no negative volumes, growth cap 1.35) are documented. Medium mesh selected for map sweeps with fine retained for final design-point check. | assessed
Numerical solver error | Verification — Calculation | 3 | 4 | Residuals reach defined targets; key QoI monitors demonstrate convergence | Convergence criteria are explicitly defined: residuals below 1e-5 for continuity, momentum, k, and ω. QoI monitors (Δp_total flat to within 0.2% over last 2000 iterations; blade torque stable) confirm solution convergence beyond residual targets. Solver settings (pressure-based coupled, second-order QUICK, reduced turbulent viscosity under-relaxation to 0.6, hybrid initialization with rotation ramp) are documented. Transient sliding-mesh uses 2° time step providing temporal resolution check. | assessed
Use error | Verification — Calculation | 3 | 3 | Boundary conditions verified against physical setup; model configuration independently checked; geometry and domain verified | Boundary conditions are fully specified and justified (velocity inlet for mass flow targets, pressure outlet at 0 Pa, smooth walls, MRF zone at 1200 RPM). Blockage ratio vs test rig cross-section and grille porosity matched within 2%. Porous-jump K-factor 3.1 matched to pressure-drop quadratic fit. Geometry simplifications (omitted internal cooling vanes, removed <2 mm features, retained turning vanes) are documented with rationale. No explicit independent reviewer sign-off is cited; run notes and scripted post-processing partially address this. | assessed
Model form | Validation — Model | 3 | 3 | Governing equation choices justified; turbulence model selection supported by physics rationale and cross-comparison | Physics regime justified: low Mach (Ma<0.15), incompressible, isothermal, no heat transfer. k-ω SST selected with low-Re wall treatment based on separation capture near hub/shroud and agreement with lab PIV tip leakage vortex pattern. Three turbulence models compared (SST, SA, RKE) on medium mesh; SST retained. Steady RANS MRF limitation near stall explicitly acknowledged. Default model constants retained with no empirical tuning. Porous-jump grille limitation (no vane-induced swirl recovery) acknowledged. | assessed
Model inputs | Validation — Model | 3 | 3 | Geometry from vendor CAD; boundary conditions from measurements or calibrated sources; input uncertainties characterized | Geometry from vendor CAD (2026-05-11) and AHU plenum Rev C. Tip clearance set to 1.5 mm per vendor drawing; ±0.3 mm tolerance explored in sensitivity. Inlet velocity set to match mass flow targets; turbulence intensity 5% with sensitivity 1–10%. Surface roughness 0 μm baseline with 50 μm sensitivity. Air density 1.185 kg/m^3 at 25°C. RPM sensitivity ±1% run. K-factor 3.1 from quadratic pressure-drop fit. Comprehensive sensitivity analysis partially substitutes for formal input uncertainty characterization; formal UQ propagation not fully quantified. | assessed
Test samples | Validation — Comparator | 2 | 2 | Test article adequately represents production geometry; sample characteristics documented | A single fan unit was tested on the AMCA 210 test stand (Report F-210-663). The report does not describe the number of units tested, unit-to-unit variability, or production representativeness beyond reference to the vendor report. Calibration documentation (pressure tap and flow nozzle calibration sheets) is included in the vendor report. No statistical characterization of sample population is presented. | assessed
Test conditions | Validation — Comparator | 3 | 3 | Calibrated instruments; measured experimental uncertainty; AMCA 210 standard compliance | Tests conducted per AMCA 210 standard. Calibration sheets for pressure taps and flow nozzle provided in vendor report. Measurement uncertainties quantified: Δp ±1.5% (95% coverage), flow ±1.0%, RPM ±0.3%. Data corrected to 25°C and sea level for comparability with CFD. Test rig schematic included. Environmental control details (beyond temperature/density correction) not described. | assessed
Equivalency of input parameters | Validation — Assessment | 3 | 3 | CFD boundary conditions match AMCA 210 test conditions; corrections and deviations documented | CFD and test conditions aligned at matching flow rates (2.0, 3.0, 4.0 m^3/s), same 1200 RPM, same air density (25°C/sea level correction applied to test data). Blockage ratio and grille porosity matched within 2%. Porous-jump K-factor derived from same pressure-drop data. Tip clearance set per vendor drawing matching test article. Steady RANS vs test rig dynamic conditions acknowledged as a gap near stall. Turbulence inlet conditions (5% TI) are an assumption not directly measured in the rig. | assessed
Output comparison | Validation — Assessment | 3 | 3 | Quantitative error metrics reported at multiple operating points; comparison within acceptance bands; uncertainty bands considered | Δp_total compared at three duty points: −6.5% at 2.0 m^3/s, −3.2% at 3.0 m^3/s, −3.1% at 4.0 m^3/s. All within stated acceptance bands (±8% off-design, ±5% design point). Resolution uncertainty (1.9% GCI) and model-form spread (~3% across RANS closures) reported alongside experimental uncertainty (±1.5%). Swirl intensity has no direct test metric; indirect traverse skewness trend agreement noted. Non-uniformity index has no direct test comparison. Quantitative combined uncertainty analysis not formally aggregated. | assessed
Relevance of the quantities of interest | Applicability | 3 | 3 | QoIs (Δp_total, swirl intensity, non-uniformity index) directly address the equipment selection decision and are measurable both computationally and experimentally | Δp_total is directly relevant to the equipment selection decision and is measurable both computationally and via AMCA 210 test. Swirl intensity and non-uniformity index are directly relevant to downstream airflow quality requirements and are computationally well-defined. Swirl intensity has only indirect experimental validation (traverse skewness trend); non-uniformity index has no direct experimental comparator in this study. This partial measurability for two of three QoIs slightly limits the level. | assessed
Relevance of the validation activities to the COU | Applicability | 3 | 3 | Validation covers the intended operating range and geometry; gaps between validation conditions and COU are identified | Validation uses the actual vendor fan geometry at operating conditions (1200 RPM, 2.0–4.0 m^3/s, 25°C, sea level) matching the COU envelope. AMCA 210 standard test directly represents the fan performance COU. Known gaps are explicitly documented: steady RANS less reliable near stall onset (2.0 m^3/s), porous-jump grille does not replicate vane-induced swirl recovery, tip clearance tolerance range not fully explored, no direct swirl or non-uniformity experimental validation. Transient sliding-mesh spot-check at design point partially addresses the steady-RANS limitation. Gaps are acknowledged as future work. | assessed
Note on C5: [Extract] ¦ Confidence: 50%
Note on D5: [Extract] ¦ Confidence: 50%
Note on E5: [Extract] ¦ Confidence: 50%
Note on F5: [Extract] ¦ Confidence: 50%
Note on G5: [Extract] ¦ Confidence: 50%
Note on C6: [Extract] ¦ Confidence: 50%
Note on D6: [Extract] ¦ Confidence: 50%
Note on E6: [Extract] ¦ Confidence: 50%
Note on F6: [Extract] ¦ Confidence: 50%
Note on G6: [Extract] ¦ Confidence: 50%
Note on C7: [Extract] ¦ Confidence: 50%
Note on D7: [Extract] ¦ Confidence: 50%
Note on E7: [Extract] ¦ Confidence: 50%
Note on F7: [Extract] ¦ Confidence: 50%
Note on G7: [Extract] ¦ Confidence: 50%
Note on C8: [Extract] ¦ Confidence: 50%
Note on D8: [Extract] ¦ Confidence: 50%
Note on E8: [Extract] ¦ Confidence: 50%
Note on F8: [Extract] ¦ Confidence: 50%
Note on G8: [Extract] ¦ Confidence: 50%
Note on C9: [Extract] ¦ Confidence: 50%
Note on D9: [Extract] ¦ Confidence: 50%
Note on E9: [Extract] ¦ Confidence: 50%
Note on F9: [Extract] ¦ Confidence: 50%
Note on G9: [Extract] ¦ Confidence: 50%
Note on C10: [Extract] ¦ Confidence: 50%
Note on D10: [Extract] ¦ Confidence: 50%
Note on E10: [Extract] ¦ Confidence: 50%
Note on F10: [Extract] ¦ Confidence: 50%
Note on G10: [Extract] ¦ Confidence: 50%
Note on C11: [Extract] ¦ Confidence: 50%
Note on D11: [Extract] ¦ Confidence: 50%
Note on E11: [Extract] ¦ Confidence: 50%
Note on F11: [Extract] ¦ Confidence: 50%
Note on G11: [Extract] ¦ Confidence: 50%
Note on C12: [Extract] ¦ Confidence: 50%
Note on D12: [Extract] ¦ Confidence: 50%
Note on E12: [Extract] ¦ Confidence: 50%
Note on F12: [Extract] ¦ Confidence: 50%
Note on G12: [Extract] ¦ Confidence: 50%
Note on C13: [Extract] ¦ Confidence: 50%
Note on D13: [Extract] ¦ Confidence: 50%
Note on E13: [Extract] ¦ Confidence: 50%
Note on F13: [Extract] ¦ Confidence: 50%
Note on G13: [Extract] ¦ Confidence: 50%
Note on C14: [Extract] ¦ Confidence: 50%
Note on D14: [Extract] ¦ Confidence: 50%
Note on E14: [Extract] ¦ Confidence: 50%
Note on F14: [Extract] ¦ Confidence: 50%
Note on G14: [Extract] ¦ Confidence: 50%
Note on C15: [Extract] ¦ Confidence: 50%
Note on D15: [Extract] ¦ Confidence: 50%
Note on E15: [Extract] ¦ Confidence: 50%
Note on F15: [Extract] ¦ Confidence: 50%
Note on G15: [Extract] ¦ Confidence: 50%
Note on C16: [Extract] ¦ Confidence: 50%
Note on D16: [Extract] ¦ Confidence: 50%
Note on E16: [Extract] ¦ Confidence: 50%
Note on F16: [Extract] ¦ Confidence: 50%
Note on G16: [Extract] ¦ Confidence: 50%
Note on C17: [Extract] ¦ Confidence: 50%
Note on D17: [Extract] ¦ Confidence: 50%
Note on E17: [Extract] ¦ Confidence: 50%
Note on F17: [Extract] ¦ Confidence: 50%
Note on G17: [Extract] ¦ Confidence: 50%

## Decision
Decision — The credibility judgment
Decision Outcome | Decision Rationale | Criteria Set | Decided By | Decision Date
Accepted | The CFD model of the 500 mm axial fan at 1200 RPM is accepted for equipment selection purposes with a 5% margin added to the required Δp at the design point. At the 3.0 m^3/s design point, predicted Δp_total is −3.2% from AMCA 210 test data, within the ±5% acceptance band; resolution uncertainty is 1.9% (GCI) and model-form spread across RANS closures is ~3%. Swirl intensity of 0.19–0.20 meets the ≤0.20 target. Off-design points (4.0 m^3/s: −3.1%; 2.0 m^3/s: −6.5%) are within the ±8% band, although the low-flow point is flagged as less robust due to steady RANS limitations near stall onset. Known limitations (steady RANS near stall, porous-jump grille approximation, absence of direct swirl/non-uniformity experimental validation) are acknowledged and do not preclude the selection decision at this stage. Recommended next steps include expanded transient coverage at low flow, broader tip-clearance tolerance study, and targeted PIV for swirl validation if scope is extended. | Auto-filled from Assessment Summary |  | 2026-08-20
Note on A3: [Extract] ¦ Confidence: 50%
Note on B3: [Extract] ¦ Confidence: 50%
Note on E3: [Extract] ¦ Confidence: 50%